CLASSIFICATION: EXERCISE ONLY

RTU PREVENTIVE MAINTENANCE SCHEDULE

VOLTANA National Grid — SCADA / Automation Department

Document Ref: VNG-SCADA-MAINT-2026-003

Sites Covered: NGP-01, NGP-02, EPS-07, SWT-12, SWT-13

Maintenance Period: Q1–Q2 2026 (January – June)

Prepared by: M. Okonkwo, SCADA Lead Engineer

Approved by: Director of Operations

# 1. Scope and Objectives

This schedule defines preventive maintenance activities for all Remote Terminal Units (RTUs) and associated SCADA communication equipment at five (5) primary substation sites. The objectives are to maintain >99.5% RTU availability, ensure data integrity to the SCADA Master Station, and comply with IEC 62443 security maintenance requirements.

# 2. Quarterly Maintenance Schedule

| Site | RTU Model | Q1 Date | Q2 Date | Technician | Est. Duration |
| --- | --- | --- | --- | --- | --- |
| NGP-01 | GE D20MX | 15 Jan 2026 | 14 Apr 2026 | J. Fernandez | 4 hrs |
| NGP-02 | GE D20MX | 17 Jan 2026 | 16 Apr 2026 | J. Fernandez | 4 hrs |
| EPS-07 | Schneider SCADAPack 334 | 22 Jan 2026 | 21 Apr 2026 | A. Petrov | 3 hrs |
| SWT-12 | Schneider SCADAPack 334 | 28 Jan 2026 | 27 Apr 2026 | A. Petrov | 3 hrs |
| SWT-13 | ABB RTU560 | 05 Feb 2026 | 05 May 2026 | M. Okonkwo | 5 hrs |

# 3. Maintenance Task Checklist

3.1  Physical and Environmental Checks

Inspect RTU enclosure for physical damage, corrosion, or pest ingress

Verify enclosure door seals and cable gland integrity

Check ambient temperature against rated operating range (typically -20°C to +60°C)

Inspect and clean cooling fans and ventilation slots

Verify earthing connections and check for continuity

3.2  Power Supply Checks

Measure DC supply voltage at RTU terminals (nominal: 48 VDC or 110 VDC, per site)

Check UPS battery charge status and estimated remaining life

Test automatic switchover to backup power supply

Record power supply voltages in maintenance log

3.3  Communication and Data Integrity

Verify all active communication links (fibre, 4G/LTE, leased line)

Confirm RTU heartbeat signal received at SCADA master

Check DNP3/IEC61850 session statistics — retries < 1%

Perform end-to-end analogue loop check on 5 random points

Verify digital input status matches physical switchgear positions

Test RTU time synchronisation accuracy (SNTP — target: ±1 ms)

3.4  Security and Firmware

Confirm firmware version against approved baseline (ref: VNG-SEC-BASELINE-2026)

Review RTU event log for unauthorised access attempts

Verify that all unused communication ports are disabled

Confirm firmware integrity check (hash verification where supported)

Update security certificate if expiry < 90 days

# 4. Completion and Sign-Off

| Item | Q1 Completed By | Q1 Date | Q2 Completed By | Q2 Date |
| --- | --- | --- | --- | --- |
| Site inspection |  |  |  |  |
| Power supply test |  |  |  |  |
| Communications check |  |  |  |  |
| Security review |  |  |  |  |
| Supervisor sign-off |  |  |  |  |