## SCADA Tag List
VOLTANA NATIONAL GRID — SCADA TAG REGISTER ¦ CLASSIFICATION: EXERCISE ONLY
Site: Northgate Primary (NGP-01) ¦ Voltage: 132/33kV ¦ Protocol: IEC 61850 / DNP3 ¦ Last Updated: 2026-02-10
Tag ID | Description | Site | Feeder/Bay | Data Type | Engineering Unit | Normal Range | Alarm Low | Alarm High | Protocol
NGP01-132-V-001 | 132kV Busbar Voltage | NGP-01 | 132kV Bus A | Analogue | kV | 128–136 | 125 | 138 | IEC61850
NGP01-132-I-001 | 132kV Incomer Current (R-phase) | NGP-01 | Incomer-1 | Analogue | A | 0–800 | 0 | 900 | IEC61850
NGP01-132-I-002 | 132kV Incomer Current (Y-phase) | NGP-01 | Incomer-1 | Analogue | A | 0–800 | 0 | 900 | IEC61850
NGP01-132-I-003 | 132kV Incomer Current (B-phase) | NGP-01 | Incomer-1 | Analogue | A | 0–800 | 0 | 900 | IEC61850
NGP01-TX1-MW | Transformer T1 Active Power | NGP-01 | TX-1 (132/33kV) | Analogue | MW | 0–80 | — | 85 | IEC61850
NGP01-TX1-MVAR | Transformer T1 Reactive Power | NGP-01 | TX-1 (132/33kV) | Analogue | MVAr | -20–20 | — | — | IEC61850
NGP01-TX1-TEMP | Transformer T1 Oil Temperature | NGP-01 | TX-1 (132/33kV) | Analogue | °C | 30–75 | — | 85 | IEC61850
NGP01-TX1-BUCHHOLZ | Transformer T1 Buchholz Relay | NGP-01 | TX-1 (132/33kV) | Digital | — | 0=Normal | — | — | IEC61850
NGP01-33-V-001 | 33kV Busbar Voltage | NGP-01 | 33kV Bus A | Analogue | kV | 31.5–34.5 | 30 | 36 | DNP3
NGP01-33-CB-F1 | 33kV Feeder 1 CB Status | NGP-01 | Feeder 1 | Digital | — | 0=Open/1=Closed | — | — | DNP3
NGP01-33-CB-F2 | 33kV Feeder 2 CB Status | NGP-01 | Feeder 2 | Digital | — | 0=Open/1=Closed | — | — | DNP3
NGP01-33-CB-F3 | 33kV Feeder 3 CB Status | NGP-01 | Feeder 3 | Digital | — | 0=Open/1=Closed | — | — | DNP3
NGP01-33-CB-F4 | 33kV Feeder 4 CB Status | NGP-01 | Feeder 4 | Digital | — | 0=Open/1=Closed | — | — | DNP3
NGP01-33-I-F1 | 33kV Feeder 1 Load Current | NGP-01 | Feeder 1 | Analogue | A | 0–400 | — | 450 | DNP3
NGP01-33-I-F2 | 33kV Feeder 2 Load Current | NGP-01 | Feeder 2 | Analogue | A | 0–400 | — | 450 | DNP3
NGP01-BATT-V | Station Battery Voltage | NGP-01 | Aux DC | Analogue | VDC | 108–120 | 105 | 125 | Modbus
NGP01-ENV-TEMP | Control Room Ambient Temp | NGP-01 | Auxiliary | Analogue | °C | 18–28 | 15 | 35 | Modbus
NGP01-SEC-DOOR | Control Room Door Status | NGP-01 | Security | Digital | — | 0=Closed | — | — | Modbus
NGP01-EARTH-FAULT | Earth Fault Protection — Bus A | NGP-01 | Protection | Digital | — | 0=Normal | — | — | IEC61850
NGP01-COMMS-RTU | RTU Communication Heartbeat | NGP-01 | SCADA | Digital | — | 1=OK | — | — | DNP3

## Control Points
SCADA Controllable Points — NGP-01 ¦ CLASSIFICATION: EXERCISE ONLY
Tag ID | Description | Control Type | Interlock | Auth Level
NGP01-33-CB-F1-CTRL | 33kV Feeder 1 CB Raise/Lower | Raise/Lower | Bus voltage > 29kV | Operator
NGP01-33-CB-F2-CTRL | 33kV Feeder 2 CB Raise/Lower | Raise/Lower | Bus voltage > 29kV | Operator
NGP01-TX1-TAP | Transformer T1 OLTC Tap Change | Increment/Decrement | Voltage within range | Operator
NGP01-132-CB-IN-CTRL | 132kV Incomer CB Trip/Close | Open/Close | Protection clear | Supervisor
NGP01-BATT-CHG | Battery Charger Enable/Disable | ON/OFF | Battery V < 115V | Technician